## Slide 1
White Paper on Hydrogen in Kenya
  —
    Calculation results

## Slide 2: Assumptions
Renewable electricity generation  reference year to be checked
Turkana central (Hybrid)
  Wind: 41.70 % capacity factor PV: 21.10 % capacity factor
Turkana south (Hybrid)
  Wind: 60.27 % capacity factor PV: 20.23 % capacity factor
Kisumu (PV)
  Wind: 12.04 % capacity factor PV: 19.77 % capacity factor
Mombasa (Wind)
  Wind: 40.40 % capacity factor PV: 17.61 % capacity factor

## Slide 3: Assumptions
Techno-economic parameters
Component | Scenario |  | CAPEX |  |  |  | OPEX |  | Lifetime |  | Efficiency
Wind |  |  | 1,238,092 | €/MW |  |  | 2.8% | of CAPEX | 25 | years | 
PV |  |  | 561,068 | €/MW |  |  | 1.7% | of CAPEX | 25 | years | 
Battery |  |  | 300,000 | €/MWh |  |  | 1.50% | of CAPEX | 15 | years | 95%
Substation |  |  | 48,928 | €/MW |  |  |  |  | 40 | years | 99.5%
Power line | 10 | MW | 40,000 | €/km |  |  | 0.7% | of CAPEX | 40 | years | Losses: 1.1% / 100 km
 | 100 | MW | 185,000 | €/km |  |  |  |  |  |  | 
 | 500 | MW | 270,000 | €/km |  |  |  |  |  |  | 
Electrolysis (PEM) | 10 | MW | 1,500,000 | €/MW | 55 % | stack share | 2% | of CAPEX | 90,000 | hours | 67%
 | 100 | MW | 1,000,000 | €/MW | 65 % | stack share |  |  |  |  | 
 | 500 | MW | 750,000 | €/MW | 71 % | stack share |  |  |  |  | 
Water treatment |  |  | 9.5 | €/(tH2O/a) |  |  | 4% | of CAPEX | 30 | years | 4.5 kWh/m³H2O
Hydrogen storage |  |  | Size dependent | €/t |  |  | 1% | of CAPEX | 30 | years | 
NH3 synthesis | 1.1 | t/h | 9,095,994 | €/(tNH3/h) |  |  | 2% | of CAPEX | 30 | years | 0.44 MWh/tNH3
 | 11.3 | t/h | 4,234,968 | €/(tNH3/h) |  |  |  |  |  |  | 
 | 56.6 | t/h | 2,481,945 | €/(tNH3/h) |  |  |  |  |  |  | 
Air separation unit |  |  | 1,450,000 | €/(tN2/h) |  |  | 2% | of CAPEX | 30 | years | 0.2 MWh/tNH3

## Slide 4: Assumptions
Scenarios
Scenario |  |  |  | Transmission line |  | Grid
 |  |  |  | km (new) | km (grid) | €/MWh
1a | Turkana central |  | 10 MW | 170 | 400 | -
1b | Wind | 41.70% | 100 MW | 170 | 400 | -
1c | PV | 21.10% | 500 MW | 570 | 0 | -
2a | Turkana south |  | 10 MW | 40 | 400 | -
2b | Wind | 60.27% | 100 MW | 40 | 400 | -
2c | PV | 20.23% | 500 MW | 440 | 0 | -
2ba | Supplementary supply from grid / geothermal PPA (auxiliaries only) |  | 100 MW | 40 | 400 | 65
2bb | Supplementary supply from grid / geothermal PPA |  | 100 MW | 40 | 400 | 65
2bc | Transport of ammonia |  | 100 MW | 40 |  | -
3a | Kisumu |  | 10 MW | 150 | 0 | -
3b | Wind | 12.04% | 100 MW | 150 | 0 | -
3c | PV | 19.77% | 500 MW | 150 | 0 | -
4a | Mombasa |  | 10 MW | 40 | 50 | -
4b | Wind | 40.40% | 100 MW | 40 | 50 | -
4c | PV | 17.16% | 500 MW | 40 | 50 | -

## Slide 5: Results
10 MW scenario
Chart: 10 MW electrolysis
| Turkana central | Turkana south | Kisumu | Mombasa
Wind | 465.3282 | 383.8876 | 0 | 476.9925
PV | 235.4537 | 139.0619 | 722.579 | 241.3558
Grid electricity | 0 | 0 | 0 | 0
Power Line | 179.6103 | 57.3278 | 280.6768 | 59.9171
Electrical infrastructure | 177.6457 | 156.0414 | 326.0222 | 182.0987
Battery | 11.0986 | 0 | 124.8879 | 11.3768
Electrolysis | 491.2872 | 460.7831 | 770.6683 | 504.7454
Water treatment | 10.1422 | 9.413 | 19.021 | 10.3964
H2 Storage | 53.5546 | 49.7043 | 100.4376 | 54.897
Ammonia synthesis | 253.732 | 247.8842 | 275.4954 | 246.4032
Air separation | 33.2678 | 32.501 | 36.1212 | 32.3069
Production | 6495 | 6998 | 3463 | 6336

## Slide 6: Results
100 MW scenario
Chart: 100 MW electrolysis
| Turkana central | Turkana south | Kisumu | Mombasa
Wind | 437.4491 | 395.2889 | 0 | 468.6947
PV | 226.3776 | 92.4967 | 660.7972 | 209.5606
Grid electricity | 0 | 0 | 0 | 0
Power Line | 99.97 | 40.1929 | 150.8527 | 40.8394
Electrical infrastructure | 50.9954 | 36.6958 | 86.8609 | 51.072
Battery | 11.7379 | 0 | 111.7269 | 0
Electrolysis | 362.4404 | 345.1139 | 562.1149 | 376.203
Water treatment | 10.7264 | 10.114 | 20.4198 | 11.0328
H2 Storage | 38.3109 | 21.6587 | 72.9323 | 39.4054
Ammonia synthesis | 118.3627 | 124.006 | 125.1816 | 121.7443
Air separation | 33.3321 | 34.9214 | 35.2524 | 34.2844
Production | 61414 | 65133 | 32260 | 59708

## Slide 7: Results
500 MW scenario
Chart: 500 MW electrolysis
| Turkana central | Turkana south | Kisumu | Mombasa
Wind | 453 | 429.8854 | 0 | 461.0821
PV | 217.5465 | 29.6618 | 633.0249 | 206.7932
Grid electricity | 0 | 0 | 0 | 0
Power Line | 99.0683 | 80.6488 | 61.8259 | 28.0221
Electrical infrastructure | 50.6959 | 32.9695 | 85.0885 | 50.9214
Battery | 0 | 0 | 114.4985 | 0
Electrolysis | 279.8504 | 277.4266 | 437.1698 | 296.8104
Water treatment | 10.6634 | 10.5409 | 20.9263 | 11.3059
H2 Storage | 21.1892 | 18.9801 | 41.5827 | 24.5061
Ammonia synthesis | 72.7914 | 75.7425 | 82.7022 | 73.1152
Air separation | 34.9773 | 36.3953 | 39.7396 | 35.1329
Production | 308885 | 312474 | 157398 | 157398

## Slide 8: Results
Turkana south
Chart: LCOA [€/t]
| 10 MW | 100 MW | 500 MW
Wind | 383.8876 | 395.2889 | 429.8854
PV | 139.0619 | 92.4967 | 29.6618
Grid electricity | 0 | 0
Power Line | 57.3278 | 40.1929 | 80.6488
Electrical infrastructure | 156.0414 | 36.6958 | 32.9695
Battery | 0 | 0 | 0
Electrolysis | 460.7831 | 345.1139 | 277.4266
Water treatment | 9.413 | 10.114 | 10.5409
H2 Storage | 49.7043 | 21.6587 | 18.9801
Ammonia synthesis | 247.8842 | 124.006 | 75.7425
Air separation | 32.501 | 34.9214 | 36.3953

## Slide 9: Results
Turkana south grid configuration / use of geothermal energy
Chart: LCOA [€/t]
| No grid electricity | Grid for auxiliaries | Grid
Wind | 395.2889 | 397.5429 | 331.0709
PV | 92.4967 | 78.7127 | 23.8369
Grid electricity | 0 | 1.8844 | 189.9012
Power Line | 40.1929 | 40.1891 | 32.4569
Electrical infrastructure | 36.6958 | 35.6324 | 25.9651
Battery | 0 | 0 | 0
Electrolysis | 345.1139 | 343.7856 | 290.4831
Water treatment | 10.114 | 10.1717 | 8.4709
H2 Storage | 21.6587 | 36.3297 | 0
Ammonia synthesis | 124.006 | 118.4775 | 103.8602
Air separation | 34.9214 | 33.3645 | 29.2481
Grid / geothermal energy
Power: 0 MWp
Energy: 0 MWh/year
Grid / geothermal energy
Power: 6.88 MWp
Energy: 1,321 MWh/year
Grid / geothermal energy
Power: 67.35 MWp
Energy: 159,876 MWh/year

## Slide 10: Results
Renewable installation
 | Wind CF | PV CF
Kisumu | 12.04% | 19.77%
Mombasa | 40.40% | 17.16%
Turkana central | 41.70% | 21.10%
Turkana south | 60.27% | 20.23%
Chart: 100 MW electrolysis
| Turkana central | Turkana south | Kisumu | Mombasa
Wind | 120 | 115 | 0 | 125
PV | 150 | 65 | 230 | 135
Battery | 10 | 0 | 50 | 0

## Slide 11: Outlook
Next steps
Reference year
  Check if the used time series are from a year that can be considered representative for the respective RE sites
„Transport of electrons vs transport of molecules“
  Challenge the set-up fot the 100 MW scenario in Turkana South by comparing the transport of electricity with the transport of the final product
    Option 1: PtX production in Nairobi, electricity transmission from RE site to PtX production site (~ 440 km)
    Option 2; PtX production near RE site, transport of ammonia to Nairobi